## PTK051-TDF 35m Tower
BOQ for PTK051 TDF Site Construction
S/N | Description | Unit | Quantity | Item Price | Total Price
Tower
1 | PTK051 TDF-35m GF self-support tower supply as per below specs. including Tower light, Grounding arrester, Grounding materials for tower, rest platforms, Ladder and cable tray (Standard Tower) • Basic wind speed : 160 Km/h • Operational wind speed :144 Km/h • Tower capability: should be at least 13.5 SQM, evenly distributed along top 10-meter • Maximum sway: +- 0.5 deg • Fabrication, galvanize and painting should be as per ( - ANSI /TIA-222-)Standard • Exposure category C, Topographic category 1, Risk Category 2) | PCs | 1 |  | 0
2 | Tower Transportation, installation, and painting (primer and two coats standard tower painting) | Job | 1 |  | 0
3 | Approximate Excavation for tower foundation in any kind of soil and transportation of the soil to safe aera and standard compaction of foundation after excavation (95%) | M3 | 135 |  | 0
4 | Stone boulder D:15cm, after compaction materials supply and work | M3 | 10 |  | 0
5 | PCC top of boulder, materials supply , work and curing | M3 | 3 |  | 0
6 | Approximate RCC for tower foundation as per tower design by (1-1-2) mark, material supply, work and 20 days curing | M3 | 28 |  | 0
7 | Pure copper rods with 16mm thickness and 3m lenght for Tower grounding according to ATOMA specification | PCs | 12 |  | 0
8 | Pure copper 70mm2 YAZD Iran made grounding cable without cover including temples, clumps, joints, Nut , Bolts and all other necessaries accessories supply and installation , for rods connection, tower legs connection and main grounding hole connection | ML | 82 |  | 0
9 | Back filling with mix material (Base course) and standard proper compaction, materials supply and work | M3 | 105 |  | 0
10 | Columns grouting after tower erection, all nut and bolt should to be covered perfectly | Job | 1 |  | 0
11 | Stone Crush supply and laying size 20mm | M3 | 14 |  | 0
Site Construction items description
12 | Excavation for boundary wall foundation (35m3), Guard room (7m3), Kitchen & bathroom (7.8m3), Generator Room (5m3), Batteries Room (0.9m3), outdoor RBS slab (3.5m3), in any type of Soil ,as per DWG | M3 | 59.2 |  | 0
13 | Gravel bedding under column footing for bounday wall column foundation with 10cm Thickness (2.2m3), | M3 | 2.2 |  | 0
14 | Stone masonry from mountain mine rocks with curing ,pointing, painting, standard 7cm PCC around the stones for boundary wall (26.12m3), Guardroom ( 4.4m3), Kitchen & bathroom (5.6m3), Generator Room (3.5m3), Batteries Room (0.75m3), RBS SLAB (4.8m3), supply of materials and work and curing, as per DWG | M3 | 45.17 |  | 0
15 | Brick masonry of boundary walls (53.9m3), Guardroom (6.5m3), Kitchen & bathroom (10.4m3), Generator Room (5.42m3), Batteries Room (1.4m3), with two-centimeter plaster to both sides, primer and 100% plastic painting, all materials supply curing and work, as per DWG | M3 | 77.62 |  | 0
16 | RCC for all column, columns foundation and ring top of stone masonry mark 200 (26.1m3), RCC ring on top of brick masonry in guard room (0.9m3), RCC ring on top of brick masonry inKitchen & bathroom (1.2m3), RCC ring on top of brick masonry in Generator Room (0.6m3), RCC ring on top of brick masonry in Batteries Room (0.15m3) | M3 | 28.95 |  | 0
17 | RCC slab for guard room roof, Mark 200 (5m3), RCC slab for Kitchen & bathroom roof (2.7m3), RCC slab for Generator Room roof(3.9m3), RCC slab for Batteries Room roof (2.07m3) and RCC for RBS slab (1.2m3) as per drawing, materials supply+ work and curing | M3 | 14.87 |  | 0
18 | PCC slab for guard room floor ( 1m3), PCC slab for Kitchen & bathroom floor (1.2m3) , PCC slab for Generator Room floor (1.32m3), PCC for Batteries Room floor (0.8m3), PCC top of Brick masonry (4m3), PCC for side walk (1.5m3) materials supply+ work and curing | M3 | 9.82 |  | 0
19 | 5cm PCC top of Izogam/ Isolation material supply, work and curing | M3 | 4.6 |  | 0
20 | Good quality 4mm isolation for guard room, Kitchen & bathroom, Generator Room, Batteries Room roofs material supply and work | M2 | 77.5 |  | 0
21 | Backfilling of guard room ( 3m3), Kitchen & bathroom (3.6m3), Generator Room (4.3m3), Batteries Room (2.4m3), Back filling for side walk (4.5m3), RBS SLAB & Shade (2.2) material supply, compaction and work | M3 | 20 |  | 0
22 | Primer and 100% plastic painting of guard room (25m2), Kitchen & bathroom (24m2), Generator Room (21.5m2), Batteries Room (22m2) all materials supply and work | M2 | 92.5 |  | 0
23 | Razor wire (600x4)mm with supporters (GI 2mm, 2"pipe Y shape) in each 2m space, three lines (171m) conventional barbed wire materials supply and proper installation | ML | 57 |  | 0
24 | Site main gate 3.5m*3m (made from closed channel + Painting, security Lock, security window ) supply, transportation, work and proper installation as per DWG | PCs | 1 |  | 0
25 | Projectors 50w with sensor and 3x4mm2 Yazd Iran cable, 10A Breaker, Pipe/ Duct-KSS for cable and clamps, materials supply and proper installation | PCs | 4 |  | 0
26 | 3" Galvanized pipe with 5mm thickness for Guardroom and Kitchen & bathroom Gutter supply and installation with elbow and clamps, as per drawing details | PCs | 2 |  | 0
27 | PVC-8000 window for guard room, double glasses, supply and proper installation as per drawing , with good quality lock and handles | M2 | 2.1 |  | 0
28 | Steel door for guard room, supply and proper installation with good quality lock and handles, as per drawing details | M2 | 2.5 |  | 0
29 | Good quality Fan supply and installation with necessary and accessory for guard room | PCs | 1 |  | 0
30 | Steel door for Kitchen & bathroom, supply and proper installation with good quality lock and handles, as per drawing details | M2 | 4 |  | 0
31 | Bathroom accessories (Soap dish, toothbrush holder, towel bars, toilet paper holders, handicap, a basin and commode supply and installation with all accessories, etc.) | Job | 1 |  | 0
32 | Exhaust fans 30cm supply and installation 1 for bathrooms and 1 for kitchen. | PCs | 2 |  | 0
33 | Kitchen set ( sink and basin ) with all necessary and accessory Supply and installation | Job | 1 |  | 0
34 | Kitchen granite tile with (330X80)cm with all necessary and accessory Supply and installation | Job | 1 |  | 0
35 | Supply and installation of ceramic tiles for floor of bathroom and kitchen (60x60) | M2 | 16 |  | 0
36 | Supply and installation of tiles for walls of bathroom and kitchen (90x30) | M2 | 42 |  | 0
37 | Complete water supply and water distribution system of Kitchen & bathroom with 500-liter water Tank supply and installation with all necessary and accessory including insulation (use 4inch best quality PVC pipe for commode outlet, 3inch best quality PVC pipe for Sink outlet, 1/2-inch PPR for clean water, all materials supply and installation) | Job | 1 |  | 0
38 | Two steel doors for Generator Room (2x2.5) and (1.3x2.5) supply and proper installation as per drawing details | M2 | 8.25 |  | 0
39 | Cable tray (350x100x1.5)mm with cover for power cable, with stands in each 50cm and all other accessories supply and installation | M3 | 10 |  | 0
40 | Steel doors for Batteries Room (1x2.5) supply and proper installation as per drawing details | M2 | 2.5 |  | 0
41 | Cable tray (350x100x1.5)mm with cover for power cable, with stands in each 50cm and all other accessories supply and installation | M3 | 10 |  | 0
42 | RBS shade L=4m, W=3m, H=3m (H=surface of slab to the bottom of truss), 22 gage sheet, Truss in each meter, truss should be made from (80x40x3)mm closed channel and closed channel top of truss (40x40x3)mm in each 0.4m c/c, piler of shade (150x150x4)mm closed channel, total of 4 piler . (100x100x4)mm closed channel ring top of steel columns and 2* (300x300x6)mm Plate and anchor bolts for each piler, including painting materials supply , work and installation | M2 | 12 |  | 0
43 | Cable tray with cover and frame from tower to RBS slab (W= 50cm and thickness= 1,5mm), as well as cover for trench in slab with dimension W= 45cmX3mm including angle ironane work materials supply and installation | ML | 10 |  | 0
Electrical and Grounding work |  |  |  |  | 0
44 | SDB 20 breakers capacity waterproof supply and installation (One in DG Room and second one to be installed under the RBS shade), the SDB should have grounding and neutral busbars and readers | PCs | 2 |  | 0
45 | 63A three phase ABB, Eco or similar quality breakers supply and installation as a main breaker for each SDB | PCs | 2 |  | 0
46 | 32A three phase ABB, Eco or similar quality breakers supply and installation, two PCs to be installed in DG room SDB for future need and two PCs in RBS SDB | PCs | 4 |  | 0
47 | 16A single phase ABB, Eco or similar quality breakers supply and installation for ordinary sockets of (Guardroom, Bathroom, Kitchen. DG Room, Batteries room, RBS shade), three PCs in RBS SDB (one for socket and two more for system use) and five PCs in DG-Room SDB (the sockets of each room should be connected by separate breaker) | PCs | 8 |  | 0
48 | 10A single phase ABB, Eco or similar quality breakers supply and installation for lighting (Guardroom, Bathroom, Kitchen. DG Room, Batteries room, RBS shade and projectors lights), two PCs in RBS SDB and four PCs in DG-Room SDB | PCs | 6 |  | 0
49 | Good quality 24W lights with accessories (Valders, 3x1.5mm2 wire, Pipe for wiring, joint, insulating tape, Join box, conduit, termination and labelling, etc...) supply and installation for Guardroom, Bathroom, Kitchen, DG Room and Batteries room, RBS shade | PCs | 12 |  | 0
50 | Good quality 24W lights with accessories (Valders, 3x1.5mm2 wire, Pipe for wiring, joint, insulating tape, Join box, conduit, termination and labelling, etc...) supply and installation for Guardroom, Bathroom, Kitchen, DG Room and Batteries room, RBS shade | PCs | 12 |  | 0
51 | Two poles Switches model Ecco or similar quality with all accessories for Guardroom, Kitchen, DG Room and Batteries room supply and installation | PCs | 4 |  | 0
52 | Two poles waterproof Switches model Ecco or similar quality with all accessories for Bathroom, RBS shade and projectors supply and installation | PCs | 3 |  | 0
53 | Good quality ordinary sockets supply and installation for Guardroom, DG Room and Batteries room , (including 3x2.5mm2 wire, Pipe for wiring, joint, insulating tape, Join box, conduit, termination and labelling, etc...) | PCs | 3 |  | 0
54 | Good quality waterproof sockets supply and installation for Bathroom, Kitchen and RBS Shade (including 3x2.5mm2 wire, Pipe for wiring, joint, insulating tape, Join box, conduit, termination and labelling, etc...) | PCs | 3 |  | 0
55 | 5x6mm2 good quality Power cable from ATS to DG-Room Fuse box including best quality 60x40 duct and proper installation, fixing and labeling supply and installation | ML | 12 |  | 0
56 | 5x10mm2 good quality Power cable from ATS to RBS Fuse box including best quality one inch PPR pipe cover for cable and proper installation, fixing and labeling supply and installation | ML | 12 |  | 0
57 | Cable tray (100x100x1.5)mm with cover for power cable from SDB to RBS, with stands in each 50cm and all other accessories supply and installation | ML | 4 |  | 0
58 | Site simple grounding, (hole dimension = 1m x 1m x 8m) making , including 4*PCs with 3m length and 16mm2 grounding pure copper rods, One PCs pure copper plates (600*600*10)mm, 35m/70mm2 copper grounding cable to connect grounding hole with busbars, 4*(400*100*10)mm grounding busbars ,48m/35mm2 grounding cable to connect accessories with busbars (main door, DGs , FT, shades , RBS, cable tray ), and 3x RCC Concrete rings and required materials for grounding hole (50Kg salt, 50Kg carbon, 50Kg cool powder, 1m3 sand) With Joints, temples and all accessories supply and installation | Job | 1 |  | 0
59 | Fire extinguisher 10kg supply and proper installation | PCs | 2 |  | 0
Solar Panels and Stand for solar Panel |  |  |  |  | 0
60 | Frame for Solar Pannels each frame should have the capacity of 12xPCs solar panels top of Roof, including RCC concrete, Main frame from U-Shape 6mm steel, 6inch with 6mm pipe as main stand, 4mm angle iron or profile for sub frame with all other accessories supply and installation | Job | 2 |  | 0
61 | Solar Pannel Grad A, 585w brand new supply and installation with clamps and all other accessories | PCs | 14 |  | 0
62 | 16mm2 best quality cable for solar to inverter and batteries with Tempol’s, joint and all other accessories | ML | 36 |  | 0
63 | Inverter PV1/PV2 best quality (approved for ATOMA and ATRA) 10 kW with all accessories supply and installation | PCs | 1 |  | 0
Generator and Fuel Tank |  |  |  |  | 0
64 | Generators transportation from ATOMA warehouse to site and proper installation | Job | 1 |  | 0
65 | 2000 Litters Fuel Tank supply and installation as per ATOMA design, the FT sould have Fuel gage and Valve + other accessories as per drawing | Job | 1 |  | 0
66 | Generators and Fuel Tank connection (Fuel flexible hope pipe steel reinforced 3/4" ID ( For diesel fuel applications), Foam for Fuel pipe good quality with 10cm thickness cover, 5x10mm2 best quality electrical cable, with clamps, cable tie, etc.. Tape, Joint, temples and all other necessaries accessories supply and installation, Fuel Pipes and cables proper management and labeling | Job | 1 |  | 0
67 | Batteries transportation and installation with all accessories | Job | 1 |  | 0
68 | ATS transportation and installation with all accessories | Job | 1 |  | 0
Access Road and Site leveling |  |  |  |  | 0
69 | Normal Access road construction as per drawing (4m wide, proper water leading trench to the hill side, Graveling and compaction) | ML | 400 |  | 0
70 | Semi Rocky Access road construction as per drawing (4m wide, proper water leading trench to the hill side, Graveling and compaction) | ML | 300 |  | 0
71 | Rocky Access road construction as per drawing (3m wide, proper water leading trench to the hill side) | ML | 0 |  | 0
72 | Site leveling | Job | 1 |  | 0
Grand Total |  |  |  |  | 0

## PTK052-TDF 35m Tower
BOQ for PTK052 TDF Site Construction
S/N | Description | Unit | Quantity | Item Price | Total Price
Tower
1 | PTK052 TDF-35m GF self-support tower supply as per below specs. including Tower light, Grounding arrester, Grounding materials for tower, rest platforms, Ladder and cable tray (Standard Tower) • Basic wind speed : 160 Km/h • Operational wind speed :144 Km/h • Tower capability: should be at least 13.5 SQM, evenly distributed along top 10-meter • Maximum sway: +- 0.5 deg • Fabrication, galvanize and painting should be as per ( - ANSI /TIA-222-)Standard • Exposure category C, Topographic category 1, Risk Category 2) | PCs | 1 |  | 0
2 | Tower Transportation, installation, and painting (primer and two coats standard tower painting) | Job | 1 |  | 0
3 | Approximate Excavation for tower foundation in any kind of soil and transportation of the soil to safe aera and standard compaction of foundation after excavation (95%) | M3 | 135 |  | 0
4 | Stone boulder D:15cm, after compaction materials supply and work | M3 | 10 |  | 0
5 | PCC top of boulder, materials supply , work and curing | M3 | 3 |  | 0
6 | Approximate RCC for tower foundation as per tower design by (1-1-2) mark, material supply, work and 20 days curing | M3 | 28 |  | 0
7 | Pure copper rods with 16mm thickness and 3m lenght for Tower grounding according to ATOMA specification | PCs | 12 |  | 0
8 | Pure copper 70mm2 YAZD Iran made grounding cable without cover including temples, clumps, joints, Nut , Bolts and all other necessaries accessories supply and installation , for rods connection, tower legs connection and main grounding hole connection | ML | 82 |  | 0
9 | Back filling with mix material (Base course) and standard proper compaction, materials supply and work | M3 | 105 |  | 0
10 | Columns grouting after tower erection, all nut and bolt should to be covered perfectly | Job | 1 |  | 0
11 | Stone Crush supply and laying size 20mm | M3 | 14 |  | 0
Site Construction items description
12 | Excavation for boundary wall foundation (35m3), Guard room (7m3), Kitchen & bathroom (7.8m3), Generator Room (5m3), Batteries Room (0.9m3), outdoor RBS slab (3.5m3), in any type of Soil ,as per DWG | M3 | 59.2 |  | 0
13 | Gravel bedding under column footing for bounday wall column foundation with 10cm Thickness (2.2m3), | M3 | 2.2 |  | 0
14 | Stone masonry from mountain mine rocks with curing ,pointing, painting, standard 7cm PCC around the stones for boundary wall (26.12m3), Guardroom ( 4.4m3), Kitchen & bathroom (5.6m3), Generator Room (3.5m3), Batteries Room (0.75m3), RBS SLAB (4.8m3), supply of materials and work and curing, as per DWG | M3 | 45.17 |  | 0
15 | Brick masonry of boundary walls (53.9m3), Guardroom (6.5m3), Kitchen & bathroom (10.4m3), Generator Room (5.42m3), Batteries Room (1.4m3), with two-centimeter plaster to both sides, primer and 100% plastic painting, all materials supply curing and work, as per DWG | M3 | 77.62 |  | 0
16 | RCC for all column, columns foundation and ring top of stone masonry mark 200 (26.1m3), RCC ring on top of brick masonry in guard room (0.9m3), RCC ring on top of brick masonry inKitchen & bathroom (1.2m3), RCC ring on top of brick masonry in Generator Room (0.6m3), RCC ring on top of brick masonry in Batteries Room (0.15m3) | M3 | 28.95 |  | 0
17 | RCC slab for guard room roof, Mark 200 (5m3), RCC slab for Kitchen & bathroom roof (2.7m3), RCC slab for Generator Room roof(3.9m3), RCC slab for Batteries Room roof (2.07m3) and RCC for RBS slab (1.2m3) as per drawing, materials supply+ work and curing | M3 | 14.87 |  | 0
18 | PCC slab for guard room floor ( 1m3), PCC slab for Kitchen & bathroom floor (1.2m3) , PCC slab for Generator Room floor (1.32m3), PCC for Batteries Room floor (0.8m3), PCC top of Brick masonry (4m3), PCC for side walk (1.5m3) materials supply+ work and curing | M3 | 9.82 |  | 0
19 | 5cm PCC top of Izogam/ Isolation material supply, work and curing | M3 | 4.6 |  | 0
20 | Good quality 4mm isolation for guard room, Kitchen & bathroom, Generator Room, Batteries Room roofs material supply and work | M2 | 77.5 |  | 0
21 | Backfilling of guard room ( 3m3), Kitchen & bathroom (3.6m3), Generator Room (4.3m3), Batteries Room (2.4m3), Back filling for side walk (4.5m3), RBS SLAB & Shade (2.2) material supply, compaction and work | M3 | 20 |  | 0
22 | Primer and 100% plastic painting of guard room (25m2), Kitchen & bathroom (24m2), Generator Room (21.5m2), Batteries Room (22m2) all materials supply and work | M2 | 92.5 |  | 0
23 | Razor wire (600x4)mm with supporters (GI 2mm, 2"pipe Y shape) in each 2m space, three lines (171m) conventional barbed wire materials supply and proper installation | ML | 57 |  | 0
24 | Site main gate 3.5m*3m (made from closed channel + Painting, security Lock, security window ) supply, transportation, work and proper installation as per DWG | PCs | 1 |  | 0
25 | Projectors 50w with sensor and 3x4mm2 Yazd Iran cable, 10A Breaker, Pipe/ Duct-KSS for cable and clamps, materials supply and proper installation | PCs | 4 |  | 0
26 | 3" Galvanized pipe with 5mm thickness for Guardroom and Kitchen & bathroom Gutter supply and installation with elbow and clamps, as per drawing details | PCs | 2 |  | 0
27 | PVC-8000 window for guard room, double glasses, supply and proper installation as per drawing , with good quality lock and handles | M2 | 2.1 |  | 0
28 | Steel door for guard room, supply and proper installation with good quality lock and handles, as per drawing details | M2 | 2.5 |  | 0
29 | Good quality Fan supply and installation with necessary and accessory for guard room | PCs | 1 |  | 0
30 | Steel door for Kitchen & bathroom, supply and proper installation with good quality lock and handles, as per drawing details | M2 | 4 |  | 0
31 | Bathroom accessories (Soap dish, toothbrush holder, towel bars, toilet paper holders, handicap, a basin and commode supply and installation with all accessories, etc.) | Job | 1 |  | 0
32 | Exhaust fans 30cm supply and installation 1 for bathrooms and 1 for kitchen. | PCs | 2 |  | 0
33 | Kitchen set ( sink and basin ) with all necessary and accessory Supply and installation | Job | 1 |  | 0
34 | Kitchen granite tile with (330X80)cm with all necessary and accessory Supply and installation | Job | 1 |  | 0
35 | Supply and installation of ceramic tiles for floor of bathroom and kitchen (60x60) | M2 | 16 |  | 0
36 | Supply and installation of tiles for walls of bathroom and kitchen (90x30) | M2 | 42 |  | 0
37 | Complete water supply and water distribution system of Kitchen & bathroom with 500-liter water Tank supply and installation with all necessary and accessory including insulation (use 4inch best quality PVC pipe for commode outlet, 3inch best quality PVC pipe for Sink outlet, 1/2-inch PPR for clean water, all materials supply and installation) | Job | 1 |  | 0
38 | Two steel doors for Generator Room (2x2.5) and (1.3x2.5) supply and proper installation as per drawing details | M2 | 8.25 |  | 0
39 | Cable tray (350x100x1.5)mm with cover for power cable, with stands in each 50cm and all other accessories supply and installation | M3 | 10 |  | 0
40 | Steel doors for Batteries Room (1x2.5) supply and proper installation as per drawing details | M2 | 2.5 |  | 0
41 | Cable tray (350x100x1.5)mm with cover for power cable, with stands in each 50cm and all other accessories supply and installation | M3 | 10 |  | 0
42 | RBS shade L=4m, W=3m, H=3m (H=surface of slab to the bottom of truss), 22 gage sheet, Truss in each meter, truss should be made from (80x40x3)mm closed channel and closed channel top of truss (40x40x3)mm in each 0.4m c/c, piler of shade (150x150x4)mm closed channel, total of 4 piler . (100x100x4)mm closed channel ring top of steel columns and 2* (300x300x6)mm Plate and anchor bolts for each piler, including painting materials supply , work and installation | M2 | 12 |  | 0
43 | Cable tray with cover and frame from tower to RBS slab (W= 50cm and thickness= 1,5mm), as well as cover for trench in slab with dimension W= 45cmX3mm including angle ironane work materials supply and installation | ML | 10 |  | 0
Electrical and Grounding work |  |  |  |  | 0
44 | SDB 20 breakers capacity waterproof supply and installation (One in DG Room and second one to be installed under the RBS shade), the SDB should have grounding and neutral busbars and readers | PCs | 2 |  | 0
45 | 63A three phase ABB, Eco or similar quality breakers supply and installation as a main breaker for each SDB | PCs | 2 |  | 0
46 | 32A three phase ABB, Eco or similar quality breakers supply and installation, two PCs to be installed in DG room SDB for future need and two PCs in RBS SDB | PCs | 4 |  | 0
47 | 16A single phase ABB, Eco or similar quality breakers supply and installation for ordinary sockets of (Guardroom, Bathroom, Kitchen. DG Room, Batteries room, RBS shade), three PCs in RBS SDB (one for socket and two more for system use) and five PCs in DG-Room SDB (the sockets of each room should be connected by separate breaker) | PCs | 8 |  | 0
48 | 10A single phase ABB, Eco or similar quality breakers supply and installation for lighting (Guardroom, Bathroom, Kitchen. DG Room, Batteries room, RBS shade and projectors lights), two PCs in RBS SDB and four PCs in DG-Room SDB | PCs | 6 |  | 0
49 | Good quality 24W lights with accessories (Valders, 3x1.5mm2 wire, Pipe for wiring, joint, insulating tape, Join box, conduit, termination and labelling, etc...) supply and installation for Guardroom, Bathroom, Kitchen, DG Room and Batteries room, RBS shade | PCs | 12 |  | 0
50 | Good quality 24W lights with accessories (Valders, 3x1.5mm2 wire, Pipe for wiring, joint, insulating tape, Join box, conduit, termination and labelling, etc...) supply and installation for Guardroom, Bathroom, Kitchen, DG Room and Batteries room, RBS shade | PCs | 12 |  | 0
51 | Two poles Switches model Ecco or similar quality with all accessories for Guardroom, Kitchen, DG Room and Batteries room supply and installation | PCs | 4 |  | 0
52 | Two poles waterproof Switches model Ecco or similar quality with all accessories for Bathroom, RBS shade and projectors supply and installation | PCs | 3 |  | 0
53 | Good quality ordinary sockets supply and installation for Guardroom, DG Room and Batteries room , (including 3x2.5mm2 wire, Pipe for wiring, joint, insulating tape, Join box, conduit, termination and labelling, etc...) | PCs | 3 |  | 0
54 | Good quality waterproof sockets supply and installation for Bathroom, Kitchen and RBS Shade (including 3x2.5mm2 wire, Pipe for wiring, joint, insulating tape, Join box, conduit, termination and labelling, etc...) | PCs | 3 |  | 0
55 | 5x6mm2 good quality Power cable from ATS to DG-Room Fuse box including best quality 60x40 duct and proper installation, fixing and labeling supply and installation | ML | 12 |  | 0
56 | 5x10mm2 good quality Power cable from ATS to RBS Fuse box including best quality one inch PPR pipe cover for cable and proper installation, fixing and labeling supply and installation | ML | 12 |  | 0
57 | Cable tray (100x100x1.5)mm with cover for power cable from SDB to RBS, with stands in each 50cm and all other accessories supply and installation | ML | 4 |  | 0
58 | Site simple grounding, (hole dimension = 1m x 1m x 8m) making , including 4*PCs with 3m length and 16mm2 grounding pure copper rods, One PCs pure copper plates (600*600*10)mm, 35m/70mm2 copper grounding cable to connect grounding hole with busbars, 4*(400*100*10)mm grounding busbars ,48m/35mm2 grounding cable to connect accessories with busbars (main door, DGs , FT, shades , RBS, cable tray ), and 3x RCC Concrete rings and required materials for grounding hole (50Kg salt, 50Kg carbon, 50Kg cool powder, 1m3 sand) With Joints, temples and all accessories supply and installation | Job | 1 |  | 0
59 | Fire extinguisher 10kg supply and proper installation | PCs | 2 |  | 0
Solar Panels and Stand for solar Panel |  |  |  |  | 0
60 | Frame for Solar Pannels each frame should have the capacity of 12xPCs solar panels top of Roof, including RCC concrete, Main frame from U-Shape 6mm steel, 6inch with 6mm pipe as main stand, 4mm angle iron or profile for sub frame with all other accessories supply and installation | Job | 2 |  | 0
61 | Solar Pannel Grad A, 585w brand new supply and installation with clamps and all other accessories | PCs | 14 |  | 0
62 | 16mm2 best quality cable for solar to inverter and batteries with Tempol’s, joint and all other accessories | ML | 36 |  | 0
63 | Inverter PV1/PV2 best quality (approved for ATOMA and ATRA) 10 kW with all accessories supply and installation | PCs | 1 |  | 0
Generator and Fuel Tank |  |  |  |  | 0
64 | Generators transportation from ATOMA warehouse to site and proper installation | Job | 1 |  | 0
65 | 2000 Litters Fuel Tank supply and installation as per ATOMA design, the FT sould have Fuel gage and Valve + other accessories as per drawing | Job | 1 |  | 0
66 | Generators and Fuel Tank connection (Fuel flexible hope pipe steel reinforced 3/4" ID ( For diesel fuel applications), Foam for Fuel pipe good quality with 10cm thickness cover, 5x10mm2 best quality electrical cable, with clamps, cable tie, etc.. Tape, Joint, temples and all other necessaries accessories supply and installation, Fuel Pipes and cables proper management and labeling | Job | 1 |  | 0
67 | Batteries transportation and installation with all accessories | Job | 1 |  | 0
68 | ATS transportation and installation with all accessories | Job | 1 |  | 0
Access Road and Site leveling |  |  |  |  | 0
69 | Normal Access road construction as per drawing (4m wide, proper water leading trench to the hill side, Graveling and compaction) | ML | 380 |  | 0
70 | Semi Rocky Access road construction as per drawing (4m wide, proper water leading trench to the hill side, Graveling and compaction) | ML | 2870 |  | 0
71 | Rocky Access road construction as per drawing (3m wide, proper water leading trench to the hill side) | ML | 400 |  | 0
72 | Site leveling | Job | 1 |  | 0
Grand Total |  |  |  |  | 0